## Main
Hardware Device
Assembly | Description | Device Name | OPC UA address | Beckhoff ADS Node Address | Beckhoff ADS port | ICD | ICD Date
HealthAndSafetyDeviceConnector | HealthAndSafetyDeviceConnector Interface | Telescope Health Control Unit | opc.tcp://127.0.0.1:52524/OPCUA/hwSimulator | 5.24.54.134.2.1 | 851 | ASTRI | 2017-02-27
HealthAndSafetyDeviceConnector | HealthAndSafetyDeviceConnector Interface | Telescope Health Control Unit | opc.tcp://192.168.100.141:4840 | 5.24.54.134.2.1 | 851 | ASTRI | 2017-02-27
Notes

## GET
Name of command | Actionee | Short name | ADS variable | OPC_UA node | OPC UA Data type | CMD/MODE value | Sampling Interval (s) | Default value | Alarm low | Alarm high | Withdraw alarm low | Withdraw alarm high | Unit | Operation modes | Expected execution time (s) | Maximum execution time (s) | IsMonitored | EngGUI | opGUI | IsArchived | Description
GET_THCU_AZLCW1 | THCU | AZLCW1 | AZ_LIMIT.AZLCW1 | ns=4;s=AZ_LIMIT.AZLCW1 | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor reports the status of the Operation limit switch for the clockwise movement. TRUE : engaged FALSE: not engaged
GET_THCU_AZLCW2 | THCU | AZLCW2 | AZ_LIMIT.AZLCW2 | ns=4;s=AZ_LIMIT.AZLCW2 | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor reports the status of the Emergency limit of the clockwise movement. TRUE : engaged FALSE: not engaged
GET_THCU_AZLCCW1 | THCU | AZLCCW1 | AZ_LIMIT.AZLCCW1 | ns=4;s=AZ_LIMIT.AZLCCW1 | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor reports the status of the Operation limit switch for the anti-clockwise movement. TRUE : engaged FALSE: not engaged
GET_THCU_AZLCCW2 | THCU | AZLCCW2 | AZ_LIMIT.AZLCCW2 | ns=4;s=AZ_LIMIT.AZLCCW2 | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor reports the status of the Emergency limit of the anti-clockwise movement. TRUE : engaged FALSE: not engaged
GET_THCU_ELOLOW | THCU | ELOLOW | EL_LIMIT.ELOLOW | ns=4;s=EL_LIMIT.ELOLOW | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor reports the status of the Operation limit switch toward the horizin direction. TRUE : engaged FALSE: not engaged
GET_THCU_ELELOW | THCU | ELELOW | EL_LIMIT.ELELOW | ns=4;s=EL_LIMIT.ELELOW | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor reports the status of the Emergency limit switch toward the horizin direction. TRUE : engaged FALSE: not engaged
GET_THCU_ELOHIGH | THCU | ELOHIGH | EL_LIMIT.ELOHIGH | ns=4;s=EL_LIMIT.ELOHIGH | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor reports the status of the Operation limit switch toward the zenith direction. TRUE : engaged FALSE: not engaged
GET_THCU_ELEHIGH | THCU | ELEHIGH | EL_LIMIT.ELEHIGH | ns=4;s=EL_LIMIT.ELEHIGH | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor reports the status of the Emergency limit switch toward the zenith direction. TRUE : engaged FALSE: not engaged
GET_THCU_AZSTOEN | THCU | AZSTOEN | AZ_STOW.AZSTOEN | ns=4;s=AZ_STOW.AZSTOEN | BOOLEAN |  | 1 | TRUE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the positioning of the AZ axis with respect the stow pin. If the AZ stow pin is aligned with the hole the value is TRUE.
GET_THCU_AZSTOIN | THCU | AZSTOIN | AZ_STOW.AZSTOIN | ns=4;s=AZ_STOW.AZSTOIN | BOOLEAN |  | 1 | TRUE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports that the AZ stow pin is completely insterted and so the axis is blocked. TRUE : inserted FALSE: not inserted
GET_THCU_AZSTOEX | THCU | AZSTOEX | AZ_STOW.AZSTOEX | ns=4;s=AZ_STOW.AZSTOEX | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports that the AZ Stow pin is completely extracted and that the axis can be moved. TRUE : extracted FALSE: not extracted
GET_THCU_ELSTOEN | THCU | ELSTOEN | EL_STOW.ELSTOEN | ns=4;s=EL_STOW.ELSTOEN | BOOLEAN |  | 1 | TRUE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the positioning of the EL axis with respect the stow pin. If the EL stow pin is aligned with the hole the value is TRUE.
GET_THCU_ELSTOIN | THCU | ELSTOIN | EL_STOW.ELSTOIN | ns=4;s=EL_STOW.ELSTOIN | BOOLEAN |  | 1 | TRUE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports that the EL stow pin is completely insterted and so the axis is blocked. TRUE : inserted FALSE: not inserted
GET_THCU_ELSTOEX | THCU | ELSTOEX | EL_STOW.ELSTOEX | ns=4;s=EL_STOW.ELSTOEX | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports that the EL Stow pin is completely extracted and that the axis can be moved. TRUE : extracted FALSE: not extracted
GET_THCU_DOORCAB | THCU | DOORCAB | EMERGENCY.DOORCAB | ns=4;s=EMERGENCY.DOORCAB | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the status of the doors of the HPC and LPC cabinet. TRUE : door open FALSE : door close
GET_THCU_DOORBASE | THCU | DOORBASE | EMERGENCY.DOORBASE | ns=4;s=EMERGENCY.DOORBASE | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the status of the door of the base. TRUE : door open FALSE : door close
GET_THCU_STOP1 | THCU | STOP1 | EMERGENCY.STOP1 | ns=4;s=EMERGENCY.STOP1 | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the status of the emergency stop of the control room (not in use for now). TRUE : energency-on FALSE : emergency-off
GET_THCU_STOP2 | THCU | STOP2 | EMERGENCY.STOP2 | ns=4;s=EMERGENCY.STOP2 | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the status of the emergency stop located in the LPC cabinet . TRUE : energency-on FALSE : emergency-off
GET_THCU_STOP_PUSH_BUTTON | THCU | STOP_PUSH_BUTTON | EMERGENCY.STOP_PUSH_BUTTON | ns=4;s=EMERGENCY.STOP_PUSH_BUTTON | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor reports the status of the emergency stop of the Mobile Push Button (MPB). TRUE : energency-on FALSE : emergency-off
GET_THCU_EMERGENCYON | THCU | EMERGENCYON | EMERGENCY.EMERGENCY_ON | ns=4;s=EMERGENCY.EMERGENCY_ON | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the status of the Safety . TRUE : one of the emergency switches is engaged, the drive system is inhibit FALSE : noone of the emergency switch is engaged
GET_THCU_OVERRIDESAFETYSTATUS | THCU | OVERRIDESAFETYSTATUS | EMERGENCY.OVER_SAFETY_STATUS | ns=4;s=EMERGENCY.OVER_SAFETY_STATUS | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the status of the Override Function for the safety logic chain. TRUE: override function is active FALSE : override function is not active
GET_THCU_ELSS1STOSIGNAL | THCU | ELSS1STOSIGNAL | MOTOR_SAFETY.EL_SS1_STO_SIGNAL | ns=4;s=MOTOR_SAFETY.EL_SS1_STO_SIGNAL | BOOLEAN |  | 1 | TRUE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the Status of the EL driver safety signal. TRUE : safety disabled, Axis ready to be activated FALSE : Safety enabled, some emergency switch engaged
GET_THCU_AZSS1STOSIGNAL | THCU | AZSS1STOSIGNAL | MOTOR_SAFETY.AZ_SS1_STO_SIGNAL | ns=4;s=MOTOR_SAFETY.AZ_SS1_STO_SIGNAL | BOOLEAN |  | 1 | TRUE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the Status of the AZ driver safety signal. TRUE : safety disabled, Axis ready to be activated FALSE : Safety enabled, some emergency switch engaged
GET_THCU_MOTORS400VONOFF | THCU | MOTORS400VONOFF | STATUSDEV.MOTORS_400V | ns=4;s=STATUSDEV.MOTORS_400V | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor reports the status of the 400V power supply at the motors. TRUE : 400V to the motors on FALSE : 400V to the motors off
GET_THCU_CAMERA_ONOFF | THCU | CAMERA_ONOFF | STATUSDEV.CAMERA | ns=4;s=STATUSDEV.CAMERA | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor report the status of Camera. TRUE : swithced-on FALSE : swithced-off
GET_THCU_DATA_LOGGER_ONOFF | THCU | DATA_LOGGER_ONOFF | STATUSDEV.DATA_LOGGER | ns=4;s=STATUSDEV.DATA_LOGGER | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor report the status of the Data Logger. TRUE : swithced-on FALSE : swithced-off
GET_THCU_M1_ONOFF | THCU | M1_ONOFF | STATUSDEV.M1 | ns=4;s=STATUSDEV.M1 | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor report the status of the M1 Boxes. TRUE : swithced-on FALSE : swithced-off
GET_THCU_M2_ONOFF | THCU | M2_ONOFF | STATUSDEV.M2 | ns=4;s=STATUSDEV.M2 | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor report the status of the M2 Boxes. TRUE : swithced-on FALSE : swithced-off
GET_THCU_PMC_ONOFF | THCU | PMC_ONOFF | STATUSDEV.PMC | ns=4;s=STATUSDEV.PMC | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor report the status of the Pointing Monitor Camera (PMC). TRUE : swithced-on FALSE : swithced-off
GET_THCU_CAMERA_TH_CONTROL_ONOFF | THCU | CAMERA_TH_CONTROL_ONOFF | STATUSDEV.CAMERA_TH_CONTROL | ns=4;s=STATUSDEV.CAMERA_TH_CONTROL | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor report the status of the Camera Thermal Control. TRUE : swithced-on FALSE : swithced-off
GET_THCU_MAINDISCONNACTORFEEDBACK | THCU | MAINDISCONNACTORFEEDBACK | STATUSDEV.MAIN_DISCONNECTOR_FEEDBACK | ns=4;s=STATUSDEV.MAIN_DISCONNECTOR_FEEDBACK | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor reports the status of the main disconnector . TRUE : swithced-on FALSE : swithced-off
GET_THCU_SQM_ONOFF | THCU | SQM_ONOFF | STATUSDEV.SQM | ns=4;s=STATUSDEV.SQM | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor report the status of the Sky Quality Meter (SQM). TRUE : swithced-on FALSE : swithced-off
GET_THCU_UVSIPM_ONOFF | THCU | UVSIPM_ONOFF | STATUSDEV.UVSIPM | ns=4;s=STATUSDEV.UVSIPM | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor report the status of the UVSIPM assembly. TRUE : swithced-on FALSE : swithced-off
GET_THCU_UVSCOPE_ONOFF | THCU | UVSCOPE_ONOFF | STATUSDEV.UVSCOPE | ns=4;s=STATUSDEV.UVSCOPE | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor report the status of the UVSCOPE assembly. TRUE : swithced-on FALSE : swithced-off
GET_THCU_AMCU_ONOFF | THCU | AMCU_ONOFF | STATUSDEV.AMCU | ns=4;s=STATUSDEV.AMCU | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor report the status of the Active Mirror Control Unit (AMCU). TRUE : swithced-on FALSE : swithced-off
GET_THCU_TCU_ONOFF | THCU | TCU_ONOFF | STATUSDEV.TCU | ns=4;s=STATUSDEV.TCU | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor report the status of the Telescope Control Unit (TCU). TRUE : swithced-on FALSE : swithced-off
GET_THCU_SQM_PMC_HEATHER_ONOFF | THCU | SQM_PMC_HEATHER_ONOFF | STATUSDEV.SQM_PMC_HEATER | ns=4;s=STATUSDEV.SQM_PMC_HEATER | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor report the status of the heater installed in the SQM/PMC assembly. TRUE : swithced-on FALSE : swithced-off
GET_THCU_AZSS1STOFEEDBACK | THCU | AZSS1STOFEEDBACK | STATUSDEV.AZ_SS1_STO_FEEDBACK | ns=4;s=STATUSDEV.AZ_SS1_STO_FEEDBACK | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor reports the status of the STO safety function for the AZ axes. TRUE : X7 AZ drives powered FALSE: X7 AZ drive not powered
GET_THCU_ELSS1STOFEEDBACK | THCU | ELSS1STOFEEDBACK | STATUSDEV.EL_SS1_STO_FEEDBACK | ns=4;s=STATUSDEV.EL_SS1_STO_FEEDBACK | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor reports the status of the safety functions SS1 and STO for the EL axis. TRUE : X7 EL drive powered FALSE: X7 EL drive not powered
GET_THCU_ETHERCATSLAVESTATUS | THCU | ETHERCATSLAVESTATUS | MONITORING.ETHCAT_SLAVE_STATUS | ns=4;s=MONITORING.ETHCAT_SLAVE_STATUS | STRING |  | 1 | 8 | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor reports the status of the slaveEtherCAT deviced. The first element of the string indicates the number of devices. Each element is separated by comma.1: INIT 2: PREOP 3: BOOT 4: SAFEOP 8: OP
GET_THCU_STATUS | THCU | STATUS | MONITORING.THCU_STATUS | ns=4;s=MONITORING.THCU_STATUS | INT16 |  | 1 | 1 | NA | 16 |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the status of the THCU. 1:Loaded 2:Standby 4:Online 8:Maintenance 16:Fault
GET_THCU_TIMESTAMP | THCU | TIMESTAMP | MONITORING.LOCAL_TIME | ns=4;s=MONITORING.LOCAL_TIME | STRING |  | NA | NA | NA | NA |  |  | UTC | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | N | This monitor reports the actual time in UTC format.
GET_THCU_CABTEMPLPC1 | THCU | CABTEMPLPC1 | MONITORING.CAB_TEMP_LPC1 | ns=4;s=MONITORING.CAB_TEMP_LPC1 | FLOAT |  | 1 | 0.0 | 0.0 | 40.0 |  |  | Deg C | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the Temperature inside the LPC cabinet (sensor1)
GET_THCU_CABTEMPLPC2 | THCU | CABTEMPLPC2 | MONITORING.CAB_TEMP_LPC2 | ns=4;s=MONITORING.CAB_TEMP_LPC2 | FLOAT |  | 1 | 0.0 | 0.0 | 40.0 |  |  | Deg C | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the Temperature inside the LPC cabinet (sensor2)
GET_THCU_CABTEMPHPC | THCU | CABTEMPHPC | MONITORING.CAB_TEMP_HPC | ns=4;s=MONITORING.CAB_TEMP_HPC | FLOAT |  | 1 | 0.0 | 0.0 | 45.0 |  |  | Deg C | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the Temperature inside the HPC cabinet
GET_THCU_PH1CURRENT | THCU | PH1CURRENT | MONITORING.PH1_CURRENT | ns=4;s=MONITORING.PH1_CURRENT | FLOAT |  | 1 | 1.6 | 0.0 | 46.0 |  |  | Ampere (A) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the first phase current measurement of the cabinet high voltage
GET_THCU_PH1VOLTAGE | THCU | PH1VOLTAGE | MONITORING.PH1_VOLTAGE | ns=4;s=MONITORING.PH1_VOLTAGE | FLOAT |  | 1 | 215.0 | 209.0 | 250.0 |  |  | Volt (V) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the first phase voltage measurement of the cabinet high voltage
GET_THCU_PH1ACTIVEPOWER | THCU | PH1ACTIVEPOWER | MONITORING.PH1_ACTIVE_POWER | ns=4;s=MONITORING.PH1_ACTIVE_POWER | FLOAT |  | 1 | 251.0 | NA | NA |  |  | Watt (W) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | This monitor reports the first phase effective power measurement of the cabinet high voltage
GET_THCU_PH1APPARENTPOWER | THCU | PH1APPARENTPOWER | MONITORING.PH1_APPARENT_POWER | ns=4;s=MONITORING.PH1_APPARENT_POWER | FLOAT |  | 1 | 0.0 | NA | NA |  |  | Volt Ampere (VA) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the first phase apparent power measurement of the motors high voltage 3 phases power supply
GET_THCU_PH1REACTIVEPOWER | THCU | PH1REACTIVEPOWER | MONITORING.PH1_REACTIVE_POWER | ns=4;s=MONITORING.PH1_REACTIVE_POWER | FLOAT |  | 1 | 0.0 | NA | NA |  |  | Volt Ampere Reactive (VAR) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | This monitor reports the first phase reactive power measurement of the motors high voltage 3 phases power supply
GET_THCU_PH1ENERGY | THCU | PH1ENERGY | MONITORING.PH1_ENERGY | ns=4;s=MONITORING.PH1_ENERGY | FLOAT |  | 1 | 570541.0 | NA | NA |  |  | Watt hour (Wh) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | This monitor reports the first phase energy measurement of the motors high voltage 3 phases power supply
GET_THCU_PH1COSPHI | THCU | PH1COSPHI | MONITORING.PH1_COSPHI | ns=4;s=MONITORING.PH1_COSPHI | FLOAT |  | 1 | 0.75 | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | This monitor reports the first phase power factor of the motors high voltage 3 phases power supply
GET_THCU_PH1FREQUENCY | THCU | PH1FREQUENCY | MONITORING.PH1_FREQUENCY | ns=4;s=MONITORING.PH1_FREQUENCY | FLOAT |  | 1 | 50.0 | 47.5 | 52.5 |  |  | Hertz (Hz) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | This monitor reports the first phase frequency of the signals of the motors high voltage 3 phases power supply
GET_THCU_PH2CURRENT | THCU | PH2CURRENT | MONITORING.PH2_CURRENT | ns=4;s=MONITORING.PH2_CURRENT | FLOAT |  | 1 | 0.16 | 0.0 | 46.0 |  |  | Ampere (A) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the second phase current measurement of the motors high voltage 3 phases power supply
GET_THCU_PH2VOLTAGE | THCU | PH2VOLTAGE | MONITORING.PH2_VOLTAGE | ns=4;s=MONITORING.PH2_VOLTAGE | FLOAT |  | 1 | 215.0 | 209.0 | 250.0 |  |  | Volt (V) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the second phase voltage measurement of the motors high voltage 3 phases power supply
GET_THCU_PH2ACTIVEPOWER | THCU | PH2ACTIVEPOWER | MONITORING.PH2_ACTIVE_POWER | ns=4;s=MONITORING.PH2_ACTIVE_POWER | FLOAT |  | 1 | 28.0 | NA | NA |  |  | Watt (W) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | This monitor reports the second phase effective power measurement of the motors high voltage 3 phases power supply
GET_THCU_PH2APPARENTPOWER | THCU | PH2APPARENTPOWER | MONITORING.PH2_APPARENT_POWER | ns=4;s=MONITORING.PH2_APPARENT_POWER | FLOAT |  | 1 | 0.0 | NA | NA |  |  | Volt Ampere (VA) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the second phase apparent power measurement of the motors high voltage 3 phases power supply
GET_THCU_PH2REACTIVEPOWER | THCU | PH2REACTIVEPOWER | MONITORING.PH2_REACTIVE_POWER | ns=4;s=MONITORING.PH2_REACTIVE_POWER | FLOAT |  | 1 | 0.0 | NA | NA |  |  | Volt Ampere Reactive (VAR) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | This monitor reports the second phase reactive power measurement of the motors high voltage 3 phases power supply
GET_THCU_PH2ENERGY | THCU | PH2ENERGY | MONITORING.PH2_ENERGY | ns=4;s=MONITORING.PH2_ENERGY | FLOAT |  | 1 | 151891.0 | NA | NA |  |  | Watt hour (Wh) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | This monitor reports the second phase energy measurement of the motors high voltage 3 phases power supply
GET_THCU_PH2COSPHI | THCU | PH2COSPHI | MONITORING.PH2_COSPHI | ns=4;s=MONITORING.PH2_COSPHI | FLOAT |  | 1 | 0.5 | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | This monitor reports the second phase power factor of the motors high voltage 3 phases power supply
GET_THCU_PH2FREQUENCY | THCU | PH2FREQUENCY | MONITORING.PH2_FREQUENCY | ns=4;s=MONITORING.PH2_FREQUENCY | FLOAT |  | 1 | 50.0 | 47.5 | 52.5 |  |  | Hertz (Hz) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | This monitor reports the second phase frequency of the signals of the motors high voltage 3 phases power supply
GET_THCU_PH3CURRENT | THCU | PH3CURRENT | MONITORING.PH3_CURRENT | ns=4;s=MONITORING.PH3_CURRENT | FLOAT |  | 1 | 1.7 | 0.0 | 46.0 |  |  | Ampere (A) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the third phase current measurement of the motors high voltage 3 phases power supply
GET_THCU_PH3VOLTAGE | THCU | PH3VOLTAGE | MONITORING.PH3_VOLTAGE | ns=4;s=MONITORING.PH3_VOLTAGE | FLOAT |  | 1 | 202.0 | 209.0 | 250.0 |  |  | Volt (V) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the third phase voltage measurement of the motors high voltage 3 phases power supply
GET_THCU_PH3ACTIVEPOWER | THCU | PH3ACTIVEPOWER | MONITORING.PH3_ACTIVE_POWER | ns=4;s=MONITORING.PH3_ACTIVE_POWER | FLOAT |  | 1 | 190.0 | NA | NA |  |  | Watt (W) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | This monitor reports the third phase effective power measurement of the motors high voltage 3 phases power supply
GET_THCU_PH3APPARENTPOWER | THCU | PH3APPARENTPOWER | MONITORING.PH3_APPARENT_POWER | ns=4;s=MONITORING.PH3_APPARENT_POWER | FLOAT |  | 1 | 0.0 | NA | NA |  |  | Volt Ampere (VA) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | This monitor reports the third phase apparent power measurement of the motors high voltage 3 phases power supply
GET_THCU_PH3REACTIVEPOWER | THCU | PH3REACTIVEPOWER | MONITORING.PH3_REACTIVE_POWER | ns=4;s=MONITORING.PH3_REACTIVE_POWER | FLOAT |  | 1 | 0.0 | NA | NA |  |  | Volt Ampere Reactive (VAR) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | This monitor reports the third phase reactive power measurement of the motors high voltage 3 phases power supply
GET_THCU_PH3ENERGY | THCU | PH3ENERGY | MONITORING.PH3_ENERGY | ns=4;s=MONITORING.PH3_ENERGY | FLOAT |  | 1 | 993844.0 | NA | NA |  |  | Watt hour (Wh) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | This monitor reports the third phase energy measurement of the motors high voltage 3 phases power supply
GET_THCU_PH3COSPHI | THCU | PH3COSPHI | MONITORING.PH3_COSPHI | ns=4;s=MONITORING.PH3_COSPHI | FLOAT |  | 1 | 0.6 | NA | NA |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | This monitor reports the third phase power factor of the motors high voltage 3 phases power supply
GET_THCU_PH3FREQUENCY | THCU | PH3FREQUENCY | MONITORING.PH3_FREQUENCY | ns=4;s=MONITORING.PH3_FREQUENCY | FLOAT |  | 1 | 50.0 | 47.5 | 52.5 |  |  | Hertz (Hz) | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | This monitor reports the third phase frequency of the signals of the motors high voltage 3 phases power supply
GET_THCU_ERROR_NUMBER | THCU | ERROR_NUMBER | DIAGNOSTIC.ERROR_NUMBER | ns=4;s=DIAGNOSTIC.ERROR_NUMBER | INT16 |  | 1 | 0 | NA | NA |  |  | NA | LOADED/STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The monitor reports the number of errors that has been occurred
GET_THCU_ERROR_INFORMATION | THCU | ERROR_INFORMATION | DIAGNOSTIC.ERROR_INFORMATION | ns=4;s=DIAGNOSTIC.ERROR_INFORMATION | STRING |  | 1 | NA | NA | NA |  |  | NA | LOADED/STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | The monitor reports the information about the required error. The format is (code,origin,class,timestamp) . Class filed 1: Alarm 2: Error 3:Warning . The timestamp is in UTC format.
GET_THCU_ERROR_RECOVERED | THCU | ERROR_RECOVERED | DIAGNOSTIC.ERROR_RECOVERED | ns=4;s=DIAGNOSTIC.ERROR_RECOVERED | STRING |  | 1 | NA | NA | NA |  |  | NA | LOADED/STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | The monitor shows the lists of error that has been occurred and recovered. (1:True,2:False). The False status means that the corresponding error has been recovered.
GET_THCU_ERROR_NUMBER_RECOVERED | THCU | ERROR_NUMBER_RECOVERED | DIAGNOSTIC.ERROR_NUMBER_RECOVERED | ns=4;s=DIAGNOSTIC.ERROR_NUMBER_RECOVERED | INT16 |  | 1 | 0 | NA | NA |  |  | NA | LOADED/STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | Y | The monitor reports the number of errors that has been recovered
GET_THCU_TCU_STATUS | THCU | TCU_STATUS | MONITORING.TCU_STATUS | ns=4;s=MONITORING.TCU_STATUS | INT16 |  | 1 | 0 | NA | 7 |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The Monitor shows the status of the TCU. 0: Loaded 1: Standby 2: Online Idle 3: Online Slew 4: Online Track 5: Calibration 6: Maintenance 7: Fault
GET_THCU_AMCU_STATUS | THCU | AMCU_STATUS | MONITORING.AMCU_STATUS | ns=4;s=MONITORING.AMCU_STATUS | INT16 |  | 1 | 0 | NA | 7 |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The Monitor shows the satus of the AMCU. 0: Loaded 1: Standby 2: Online Idle 8:Online Move 7: Fault
GET_THCU_CAMERA_STATUS | THCU | CAMERA_STATUS | MONITORING.CAMERA_STATUS | ns=4;s=MONITORING.CAMERA_STATUS | INT16 |  | 1 | 0 | NA | 7 |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The Monitor shows the satus of the CAMERA.0: Loaded 1: Standby 2: Online Idle 9: Scientific 5: Calibration 6: Maintenance 7: Fault
GET_THCU_PMC_STATUS | THCU | PMC_STATUS | MONITORING.PMC_STATUS | ns=4;s=MONITORING.PMC_STATUS | INT16 |  | 1 | 0 | NA | 7 |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The Monitor shows the satus of the PMC.0: Loaded 1:Standby 2:Online Idle 3: Online Busy 7: Fault
GET_THCU_UVSIPM_STATUS | THCU | UVSIPM_STATUS | MONITORING.UVSIPM_STATUS | ns=4;s=MONITORING.UVSIPM_STATUS | INT16 |  | 1 | 0 | NA | 7 |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The Monitor shows the satus of the UVSIPM.0: Loaded 1: Standby 2: Online Idle 5: Calibration 6: Maintenance 7: Fault
GET_THCU_UVSCOPE_STATUS | THCU | UVSCOPE_STATUS | MONITORING.UVSCOPE_STATUS | ns=4;s=MONITORING.UVSCOPE_STATUS | INT16 |  | 1 | 0 | NA | 7 |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The Monitor shows the satus of the UVSCOPE.0: Loaded 1: Standby 2: Online Idle 5: Calibration 6: Maintenance 7: Fault
GET_THCU_SQM_STATUS | THCU | SQM_STATUS | MONITORING.SQM_STATUS | ns=4;s=MONITORING.SQM_STATUS | INT16 |  | 1 | 0 | NA | 7 |  |  | NA | STBY/ONLINE/MAINT/CALIB/FAULT |  |  | Y |  |  | Y | The Monitor shows the satus of the SQM.0: Loaded 1: Standby 2: Online 7: Fault
GET_THCU_HEARTBEAT | THCU | HEARTBEAT | MONITORING.HEARTBEAT | ns=4;s=MONITORING.HEARTBEAT | INT32 |  | NA | 0 | 0 | 86400 |  |  | NA | LOADED/STBY/ONLINE/MAINT/CALIB/FAULT |  |  | N |  |  | N | The Monitor report the activities of the THMS increasing a value every 1 seconds. Every 86400 seconds (1 day) the value will be reset to zero value.
GET_THCU_AZ_STOWPINSTATUS | THCU | AZ_STOWPINSTATUS | MONITORING.AZ_STOWPIN_STATUS | ns=4;s=MONITORING.AZ_STOWPIN_STATUS | INT16 |  | 1 | 2 | NA | NA |  |  | NA | STBY/ONLINE/MAINT/FAULT |  |  | Y |  |  | Y | The monitor shows the status of the AZ Stow Pin. 0: Undefined 1: Inserting 2: Insertion Completed 3: Insertion Stopped 4: Extracting 5: Extraction Completed 6: Extraction Stopped
GET_THCU_EL_STOWPINSTATUS | THCU | EL_STOWPINSTATUS | MONITORING.EL_STOWPIN_STATUS | ns=4;s=MONITORING.EL_STOWPIN_STATUS | INT16 |  | 1 | 2 | NA | NA |  |  | NA | STBY/ONLINE/MAINT/FAULT |  |  | Y |  |  | Y | The monitor shows the status of the EL Stow Pin. 0: Undefined 1: Inserting 2: Insertion Completed 3: Insertion Stopped 4: Extracting 5: Extraction Completed 6: Extraction Stopped
GET_THCU_INHIBITFAULTSTATUS | THCU | INHIBITFAULTSTATUS | COMMAND.INHIBIT_FAULT | ns=4;s=COMMAND.INHIBIT_FAULT | BOOLEAN |  | 1 | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/FAULT |  |  | N |  |  | Y | This monitor shows the the inhibit fault status
GET_THCU_AZ_ENABLE_STATUS | THCU | AZ_ENABLE_STATUS | MONITORING.AZ_AXIS_ENABLED | ns=4;s=MONITORING.AZ_AXIS_ENABLED | BOOLEAN |  | NA | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/FAULT |  |  | N |  |  | Y | This monitor shows the AZ drives status
GET_THCU_EL_ENABLE_STATUS | THCU | EL_ENABLE_STATUS | MONITORING.EL_AXIS_ENABLED | ns=4;s=MONITORING.EL_AXIS_ENABLED | BOOLEAN |  | NA | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/FAULT |  |  | N |  |  | Y | This monitor shows the EL drives status
GET_THCU_OVERRIDE_PIN_ALARM_ONOFF | THCU | OVERRIDE_PIN_ALARM_ONOFF | COMMAND.OVERRIDE_PIN_ALARM | ns=4;s=COMMAND.OVERRIDE_PIN_ALARM | BOOLEAN |  | NA | FALSE | NA | NA |  |  | NA | STBY/ONLINE/MAINT/FAULT |  |  | N |  |  | Y | This monitor shows the override status to the Alarm of the Stow Pin limit switch.

## SET
Name of command | Actionee | Short name | ADS variable | OPC_UA node | OPC UA Data type | CMD/MODE value | Sampling Interval (s) | Default value | Alarm low | Alarm high | Withdraw alarm low | Withdraw alarm high | Unit | Unit | Operation modes | Expected execution time (s) | Maximum execution time (s) | IsMonitored | IsArchived | EngGUI | opGUI | Actor | Description
SET_THCU_AC400V_HIGHALARM | THCU | AC400V_HIGHALARM | SET.AC400V_HIGH_ALARM | ns=4;s=SET.AC400V_HIGH_ALARM | FLOAT |  |  | 414.0 | 346.0 | 414.0 |  |  |  | Volt | MAINTENANCE | [6 empty] | ENG | This variable sets a threshold at the 400VAC power distribution for the alarm upper limit
SET_THCU_AC400V_HIGHWARNING | THCU | AC400V_HIGHWARNING | SET.AC400V_HIGH_WARNING | ns=4;s=SET.AC400V_HIGH_WARNING | FLOAT |  |  | 399.9 | 361.0 | 399.9 |  |  |  | Volt | MAINTENANCE | [6 empty] | ENG | This variable sets a threshold at the 400VAC power distribution for the warning upper limit
SET_THCU_AC400V_LOWALARM | THCU | AC400V_LOWALARM | SET.AC400V_LOW_ALARM | ns=4;s=SET.AC400V_LOW_ALARM | FLOAT |  |  | 346.0 | 346.0 | 414.0 |  |  |  | Volt | MAINTENANCE | [6 empty] | ENG | This variable sets a threshold at the 400VAC power distribution for the alarm lower limit
SET_THCU_AC400V_LOWWARNING | THCU | AC400V_LOWWARNING | SET.AC400V_LOW_WARNING | ns=4;s=SET.AC400V_LOW_WARNING | FLOAT |  |  | 361.0 | 361.0 | 399.9 |  |  |  | Volt | MAINTENANCE | [6 empty] | ENG | This variable sets a threshold at the 400VAC power distribution for the warning lower limit
SET_THCU_MAXT_LPC_EMERGENCY | THCU | MAXT_LPC_EMERGENCY | SET.MAXT_LPC_CAB_EMERGENCY | ns=4;s=SET.MAXT_LPC_CAB_EMERGENCY | FLOAT |  |  | 40.0 | 0.0 | 40.0 |  |  |  | deg C | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable temperature in the LPC. If the temperature is reached all the electronic will be switched off.
SET_THCU_MAXT_LPC_WARNING | THCU | MAXT_LPC_WARNING | SET.MAXT_LPC_CAB_WARNING | ns=4;s=SET.MAXT_LPC_CAB_WARNING | FLOAT |  |  | 35.0 | 5.0 | 35.0 |  |  |  | deg C | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable temperature for the warning in the LPC.
SET_THCU_MAXT_HPC_EMERGENCY | THCU | MAXT_HPC_EMERGENCY | SET.MAXT_HPC_CAB_EMERGENCY | ns=4;s=SET.MAXT_HPC_CAB_EMERGENCY | FLOAT |  |  | 45.0 | 0.0 | 45.0 |  |  |  | deg C | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable temperature in the HPC. If the temperature is reached all the electronic will be switched off.
SET_THCU_MAXT_HPC_WARNING | THCU | MAXT_HPC_WARNING | SET.MAXT_HPC_CAB_WARNING | ns=4;s=SET.MAXT_HPC_CAB_WARNING | FLOAT |  |  | 40.0 | 5.0 | 40.0 |  |  |  | deg C | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable temperature for the warning in the HPC.
SET_THCU_MINT_LPC_EMERGENCY | THCU | MINT_LPC_EMERGENCY | SET.MINT_LPC_CAB_EMERGENCY | ns=4;s=SET.MINT_LPC_CAB_EMERGENCY | FLOAT |  |  | 0.0 | 0.0 | 40.0 |  |  |  | deg C | MAINTENANCE | [6 empty] | ENG | This variable sets the min temperature in the control cabinet (TBC)
SET_THCU_MINT_LPC_WARNING | THCU | MINT_LPC_WARNING | SET.MINT_LPC_CAB_WARNING | ns=4;s=SET.MINT_LPC_CAB_WARNING | FLOAT |  |  | 5.0 | 5.0 | 35.0 |  |  |  | deg C | MAINTENANCE | [6 empty] | ENG | This variable sets the Min temperature for the warning in the control cabinet
SET_THCU_MINT_HPC_EMERGENCY | THCU | MINT_HPC_EMERGENCY | SET.MINT_HPC_CAB_EMERGENCY | ns=4;s=SET.MINT_HPC_CAB_EMERGENCY | FLOAT |  |  | 0.0 | 0.0 | 45.0 |  |  |  | deg C | MAINTENANCE | [6 empty] | ENG | This variable sets the min temperature for the warning in the power cabinet (TBC)
SET_THCU_MINT_HPC_WARNING | THCU | MINT_HPC_WARNING | SET.MINT_HPC_CAB_WARNING | ns=4;s=SET.MINT_HPC_CAB_WARNING | FLOAT |  |  | 5.0 | 5.0 | 40.0 |  |  |  | deg C | MAINTENANCE | [6 empty] | ENG | This variable sets the Min temperature for the warning in the power cabinet
SET_THCU_PH1_CURRENT_MAX | THCU | PH1_CURRENT_MAX | SET.PH1_CURRENT_MAX | ns=4;s=SET.PH1_CURRENT_MAX | FLOAT |  |  | 46.0 | 0.0 | 46.0 |  |  | Ampère (A) | Ampere | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable first phase current of high voltage power supply
SET_THCU_PH1_CURRENT_MIN | THCU | PH1_CURRENT_MIN | SET.PH1_CURRENT_MIN | ns=4;s=SET.PH1_CURRENT_MIN | FLOAT |  |  | 0.0 | 0.0 | 46.0 |  |  | Ampère (A) | Ampere | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable first phase current of high voltage power supply
SET_THCU_PH1_VOLTAGE_MAX | THCU | PH1_VOLTAGE_MAX | SET.PH1_VOLTAGE_MAX | ns=4;s=SET.PH1_VOLTAGE_MAX | FLOAT |  |  | 250.0 | 209.0 | 250.0 |  |  | Volt (V) | Volt | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable first phase voltage of high voltage power supply
SET_THCU_PH1_VOLTAGE_MIN | THCU | PH1_VOLTAGE_MIN | SET.PH1_VOLTAGE_MIN | ns=4;s=SET.PH1_VOLTAGE_MIN | FLOAT |  |  | 209.0 | 209.0 | 250.0 |  |  | Volt (V) | Volt | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable first phase voltage of high voltage power supply
SET_THCU_PH1_ACTIVEPOWER_MAX | THCU | PH1_ACTIVEPOWER_MAX | SET.PH1_ACTIVE_POWER_MAX | ns=4;s=SET.PH1_ACTIVE_POWER_MAX | FLOAT |  |  | NA | NA | NA |  |  | Watt (W) | Wat | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable first phase effective power of high voltage power supply
SET_THCU_PH1_ACTIVEPOWER_MIN | THCU | PH1_ACTIVEPOWER_MIN | SET.PH1_ACTIVE_POWER_MIN | ns=4;s=SET.PH1_ACTIVE_POWER_MIN | FLOAT |  |  | NA | NA | NA |  |  | Watt (W) | Watt | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable first phase effective power of high voltage power supply
SET_THCU_PH1_APPARENTPOWER_MAX | THCU | PH1_APPARENTPOWER_MAX | SET.PH1_APPARENT_POWER_MAX | ns=4;s=SET.PH1_APPARENT_POWER_MAX | FLOAT |  |  | NA | NA | NA |  |  | Volt Ampère (VA) | Volt Ampere | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable first phase apparent power of high voltage power supply
SET_THCU_PH1_APPARENTPOWER_MIN | THCU | PH1_APPARENTPOWER_MIN | SET.PH1_APPARENT_POWER_MIN | ns=4;s=SET.PH1_APPARENT_POWER_MIN | FLOAT |  |  | NA | NA | NA |  |  | Volt Ampère (VA) | Volt Ampere | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable first phase apparent power of high voltage power supply
SET_THCU_PH1_REACTIVEPOWER_MAX | THCU | PH1_REACTIVEPOWER_MAX | SET.PH1_REACTIVE_POWER_MAX | ns=4;s=SET.PH1_REACTIVE_POWER_MAX | FLOAT |  |  | NA | NA | NA |  |  | Volt Ampère Reactive (VAR) | VAR | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable first phase reactive power of high voltage power supply
SET_THCU_PH1_REACTIVEPOWER_MIN | THCU | PH1_REACTIVEPOWER_MIN | SET.PH1_REACTIVE_POWER_MIN | ns=4;s=SET.PH1_REACTIVE_POWER_MIN | FLOAT |  |  | NA | NA | NA |  |  | Volt Ampère Reactive (VAR) | VAR | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable first phase reactive power of high voltage power supply
SET_THCU_PH1_ENERGY_MAX | THCU | PH1_ENERGY_MAX | SET.PH1_ENERGY_MAX | ns=4;s=SET.PH1_ENERGY_MAX | FLOAT |  |  | NA | NA | NA |  |  | Watt hour (Wh) | Wh | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable first phase energy of high voltage power supply
SET_THCU_PH1_ENERGY_MIN | THCU | PH1_ENERGY_MIN | SET.PH1_ENERGY_MIN | ns=4;s=SET.PH1_ENERGY_MIN | FLOAT |  |  | NA | NA | NA |  |  | Watt hour (Wh) | Wh | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable first phase energy of high voltage power supply
SET_THCU_PH1_COSPHI_MAX | THCU | PH1_COSPHI_MAX | SET.PH1_COSPHI_MAX | ns=4;s=SET.PH1_COSPHI_MAX | FLOAT |  |  | NA | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable first phase power factor of high voltage power supply
SET_THCU_PH1_COSPHI_MIN | THCU | PH1_COSPHI_MIN | SET.PH1_COSPHI_MIN | ns=4;s=SET.PH1_COSPHI_MIN | FLOAT |  |  | NA | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable first phase power factor of high voltage power supply
SET_THCU_PH1_FREQUENCY_MAX | THCU | PH1_FREQUENCY_MAX | SET.PH1_FREQUENCY_MAX | ns=4;s=SET.PH1_FREQUENCY_MAX | FLOAT |  |  | 52.5 | 47.5 | 52.5 |  |  | Hertz (Hz) | Hz | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable first phase frequency of high voltage power supply
SET_THCU_PH1_FREQUENCY_MIN | THCU | PH1_FREQUENCY_MIN | SET.PH1_FREQUENCY_MIN | ns=4;s=SET.PH1_FREQUENCY_MIN | FLOAT |  |  | 47.5 | 47.5 | 52.5 |  |  | Hertz (Hz) | Hz | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable first phase frequency of high voltage power supply
SET_THCU_PH2_CURRENT_MAX | THCU | PH2_CURRENT_MAX | SET.PH2_CURRENT_MAX | ns=4;s=SET.PH2_CURRENT_MAX | FLOAT |  |  | 46.0 | 0.0 | 46.0 |  |  | Ampère (A) | Ampere | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable second phase current of high voltage power supply
SET_THCU_PH2_CURRENT_MIN | THCU | PH2_CURRENT_MIN | SET.PH2_CURRENT_MIN | ns=4;s=SET.PH2_CURRENT_MIN | FLOAT |  |  | 0.0 | 0.0 | 46.0 |  |  | Ampère (A) | Ampere | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable second phase current of high voltage power supply
SET_THCU_PH2_VOLTAGE_MAX | THCU | PH2_VOLTAGE_MAX | SET.PH2_VOLTAGE_MAX | ns=4;s=SET.PH2_VOLTAGE_MAX | FLOAT |  |  | 250.0 | 209.0 | 250.0 |  |  | Volt (V) | Volt | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable second phase voltage of high voltage power supply
SET_THCU_PH2_VOLTAGE_MIN | THCU | PH2_VOLTAGE_MIN | SET.PH2_VOLTAGE_MIN | ns=4;s=SET.PH2_VOLTAGE_MIN | FLOAT |  |  | 209.0 | 209.0 | 250.0 |  |  | Volt (V) | Volt | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable second phase voltage of high voltage power supply
SET_THCU_PH2_ACTIVEPOWER_MAX | THCU | PH2_ACTIVEPOWER_MAX | SET.PH2_ACTIVE_POWER_MAX | ns=4;s=SET.PH2_ACTIVE_POWER_MAX | FLOAT |  |  | NA | NA | NA |  |  | Watt (W) | Wat | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable second phase effective power of high voltage power supply
SET_THCU_PH2_ACTIVEPOWER_MIN | THCU | PH2_ACTIVEPOWER_MIN | SET.PH2_ACTIVE_POWER_MIN | ns=4;s=SET.PH2_ACTIVE_POWER_MIN | FLOAT |  |  | NA | NA | NA |  |  | Watt (W) | Watt | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable second phase effective power of high voltage power supply
SET_THCU_PH2_APPARENTPOWER_MAX | THCU | PH2_APPARENTPOWER_MAX | SET.PH2_APPARENT_POWER_MAX | ns=4;s=SET.PH2_APPARENT_POWER_MAX | FLOAT |  |  | NA | NA | NA |  |  | Volt Ampère (VA) | Volt Ampere | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable second phase apparent power of high voltage power supply
SET_THCU_PH2_APPARENTPOWER_MIN | THCU | PH2_APPARENTPOWER_MIN | SET.PH2_APPARENT_POWER_MIN | ns=4;s=SET.PH2_APPARENT_POWER_MIN | FLOAT |  |  | NA | NA | NA |  |  | Volt Ampère (VA) | Volt Ampere | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable second phase apparent power of high voltage power supply
SET_THCU_PH2_REACTIVEPOWER_MAX | THCU | PH2_REACTIVEPOWER_MAX | SET.PH2_REACTIVE_POWER_MAX | ns=4;s=SET.PH2_REACTIVE_POWER_MAX | FLOAT |  |  | NA | NA | NA |  |  | Volt Ampère Reactive (VAR) | VAR | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable second phase reactive power of high voltage power supply
SET_THCU_PH2_REACTIVEPOWER_MIN | THCU | PH2_REACTIVEPOWER_MIN | SET.PH2_REACTIVE_POWER_MIN | ns=4;s=SET.PH2_REACTIVE_POWER_MIN | FLOAT |  |  | NA | NA | NA |  |  | Volt Ampère Reactive (VAR) | VAR | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable second phase reactive power of high voltage power supply
SET_THCU_PH2_ENERGY_MAX | THCU | PH2_ENERGY_MAX | SET.PH2_ENERGY_MAX | ns=4;s=SET.PH2_ENERGY_MAX | FLOAT |  |  | NA | NA | NA |  |  | Watt hour (Wh) | Wh | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable second phase energy of high voltage power supply
SET_THCU_PH2_ENERGY_MIN | THCU | PH2_ENERGY_MIN | SET.PH2_ENERGY_MIN | ns=4;s=SET.PH2_ENERGY_MIN | FLOAT |  |  | NA | NA | NA |  |  | Watt hour (Wh) | Wh | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable second phase energy of high voltage power supply
SET_THCU_PH2_COSPHI_MAX | THCU | PH2_COSPHI_MAX | SET.PH2_COSPHI_MAX | ns=4;s=SET.PH2_COSPHI_MAX | FLOAT |  |  | NA | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable second phase power factor of high voltage power supply
SET_THCU_PH2_COSPHI_MIN | THCU | PH2_COSPHI_MIN | SET.PH2_COSPHI_MIN | ns=4;s=SET.PH2_COSPHI_MIN | FLOAT |  |  | NA | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable second phase power factor of high voltage power supply
SET_THCU_PH2_FREQUENCY_MAX | THCU | PH2_FREQUENCY_MAX | SET.PH2_FREQUENCY_MAX | ns=4;s=SET.PH2_FREQUENCY_MAX | FLOAT |  |  | 52.5 | 47.5 | 52.5 |  |  | Hertz (Hz) | Hz | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable second phase frequency of high voltage power supply
SET_THCU_PH2_FREQUENCY_MIN | THCU | PH2_FREQUENCY_MIN | SET.PH2_FREQUENCY_MIN | ns=4;s=SET.PH2_FREQUENCY_MIN | FLOAT |  |  | 47.5 | 47.5 | 52.5 |  |  | Hertz (Hz) | Hz | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable second phase frequency of high voltage power supply
SET_THCU_PH3_CURRENT_MAX | THCU | PH3_CURRENT_MAX | SET.PH3_CURRENT_MAX | ns=4;s=SET.PH3_CURRENT_MAX | FLOAT |  |  | 46.0 | 0.0 | 46.0 |  |  | Ampère (A) | Ampere | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable third phase current of high voltage power supply
SET_THCU_PH3_CURRENT_MIN | THCU | PH3_CURRENT_MIN | SET.PH3_CURRENT_MIN | ns=4;s=SET.PH3_CURRENT_MIN | FLOAT |  |  | 0.0 | 0.0 | 46.0 |  |  | Ampère (A) | Ampere | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable third phase current of high voltage power supply
SET_THCU_PH3_VOLTAGE_MAX | THCU | PH3_VOLTAGE_MAX | SET.PH3_VOLTAGE_MAX | ns=4;s=SET.PH3_VOLTAGE_MAX | FLOAT |  |  | 250.0 | 209.0 | 250.0 |  |  | Volt (V) | Volt | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable third phase voltage of high voltage power supply
SET_THCU_PH3_VOLTAGE_MIN | THCU | PH3_VOLTAGE_MIN | SET.PH3_VOLTAGE_MIN | ns=4;s=SET.PH3_VOLTAGE_MIN | FLOAT |  |  | 209.0 | 209.0 | 250.0 |  |  | Volt (V) | Volt | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable third phase voltage of high voltage power supply
SET_THCU_PH3_ACTIVEPOWER_MAX | THCU | PH3_ACTIVEPOWER_MAX | SET.PH3_ACTIVE_POWER_MAX | ns=4;s=SET.PH3_ACTIVE_POWER_MAX | FLOAT |  |  | NA | NA | NA |  |  | Watt (W) | Wat | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable third phase effective power of high voltage power supply
SET_THCU_PH3_ACTIVEPOWER_MIN | THCU | PH3_ACTIVEPOWER_MIN | SET.PH3_ACTIVE_POWER_MIN | ns=4;s=SET.PH3_ACTIVE_POWER_MIN | FLOAT |  |  | NA | NA | NA |  |  | Watt (W) | Watt | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable third phase effective power of high voltage power supply
SET_THCU_PH3_APPARENTPOWER_MAX | THCU | PH3_APPARENTPOWER_MAX | SET.PH3_APPARENT_POWER_MAX | ns=4;s=SET.PH3_APPARENT_POWER_MAX | FLOAT |  |  | NA | NA | NA |  |  | Volt Ampère (VA) | Volt Ampere | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable third phase apparent power of high voltage power supply
SET_THCU_PH3_APPARENTPOWER_MIN | THCU | PH3_APPARENTPOWER_MIN | SET.PH3_APPARENT_POWER_MIN | ns=4;s=SET.PH3_APPARENT_POWER_MIN | FLOAT |  |  | NA | NA | NA |  |  | Volt Ampère (VA) | Volt Ampere | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable third phase apparent power of high voltage power supply
SET_THCU_PH3_REACTIVEPOWER_MAX | THCU | PH3_REACTIVEPOWER_MAX | SET.PH3_REACTIVE_POWER_MAX | ns=4;s=SET.PH3_REACTIVE_POWER_MAX | FLOAT |  |  | NA | NA | NA |  |  | Volt Ampère Reactive (VAR) | VAR | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable third phase reactive power of high voltage power supply
SET_THCU_PH3_REACTIVEPOWER_MIN | THCU | PH3_REACTIVEPOWER_MIN | SET.PH3_REACTIVE_POWER_MIN | ns=4;s=SET.PH3_REACTIVE_POWER_MIN | FLOAT |  |  | NA | NA | NA |  |  | Volt Ampère Reactive (VAR) | VAR | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable third phase reactive power of high voltage power supply
SET_THCU_PH3_ENERGY_MAX | THCU | PH3_ENERGY_MAX | SET.PH3_ENERGY_MAX | ns=4;s=SET.PH3_ENERGY_MAX | FLOAT |  |  | NA | NA | NA |  |  | Watt hour (Wh) | Wh | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable third phase energy of high voltage power supply
SET_THCU_PH3_ENERGY_MIN | THCU | PH3_ENERGY_MIN | SET.PH3_ENERGY_MIN | ns=4;s=SET.PH3_ENERGY_MIN | FLOAT |  |  | NA | NA | NA |  |  | Watt hour (Wh) | Wh | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable third phase energy of high voltage power supply
SET_THCU_PH3_COSPHI_MAX | THCU | PH3_COSPHI_MAX | SET.PH3_COSPHI_MAX | ns=4;s=SET.PH3_COSPHI_MAX | FLOAT |  |  | NA | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable third phase power factor of high voltage power supply
SET_THCU_PH3_COSPHI_MIN | THCU | PH3_COSPHI_MIN | SET.PH3_COSPHI_MIN | ns=4;s=SET.PH3_COSPHI_MIN | FLOAT |  |  | NA | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable third phase power factor of high voltage power supply
SET_THCU_PH3_FREQUENCY_MAX | THCU | PH3_FREQUENCY_MAX | SET.PH3_FREQUENCY_MAX | ns=4;s=SET.PH3_FREQUENCY_MAX | FLOAT |  |  | 52.5 | 47.5 | 52.5 |  |  | Hertz (Hz) | Hz | MAINTENANCE | [6 empty] | ENG | This variable sets the max acceptable third phase frequency of high voltage power supply
SET_THCU_PH3_FREQUENCY_MIN | THCU | PH3_FREQUENCY_MIN | SET.PH3_FREQUENCY_MIN | ns=4;s=SET.PH3_FREQUENCY_MIN | FLOAT |  |  | 47.5 | 47.5 | 52.5 |  |  | Hertz (Hz) | Hz | MAINTENANCE | [6 empty] | ENG | This variable sets the min acceptable third phase frequency of high voltage power supply
SET_THCU_WATCHDOG | THCU | WATCHDOG | SET.WATCHDOG | ns=4;s=SET.WATCHDOG | INT16 |  |  | 0 | 0 | 86400 |  |  |  | NA | LOADED/STBY/ONLINE/MAINT/FAULT | [6 empty] | TCS | This variable report the activities of the ACS connection increasing a value every 1 seconds. Every 86400 seconds (1 day) the value will be reset to zero value.
SET_THCU_HERTBEATSAMPLINGTIME | THCU | HERTBEATSAMPLINGTIME | SET.SAMPLING_TIME | ns=4;s=SET.SAMPLING_TIME | INT32 |  |  | 1 | 0 | 86400 |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the sampling time for the heart beat signal.
SET_THCU_HERTBEATRESET | THCU | HERTBEATRESET | SET.RESET_HEARTBEAT | ns=4;s=SET.RESET_HEARTBEAT | INT32 |  |  | 86400 | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the maximum value of the heartbeat over which it will be reset to the zero value (default 86400 s)
SET_THCU_CURRTRANSFRATIO | THCU | CURRTRANSFRATIO | SET.CURR_TRANSF_RATIO | ns=4;s=SET.CURR_TRANSF_RATIO | FLOAT |  |  | 40.0 | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the current transformation ratio for the 3 phase High Voltage Monitoring
SET_THCU_CURRSCALEFACTOR | THCU | CURRSCALEFACTOR | SET.CURR_SCALE_FACTOR | ns=4;s=SET.CURR_SCALE_FACTOR | FLOAT |  |  | 0.000005 | NA | NA |  |  |  | Ampere | MAINTENANCE | [6 empty] | ENG | This variable sets the scale factor for the current 3 phase monitoring (A)
SET_THCU_VOLTAGESCALEFACTOR | THCU | VOLTAGESCALEFACTOR | SET.VOLTAGE_SCALE_FACTOR | ns=4;s=SET.VOLTAGE_SCALE_FACTOR | FLOAT |  |  | 0.0001 | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the scale factor for the voltage 3 phase monitoring (V)
SET_THCU_ACTPOWSCALEFACTOR | THCU | ACTPOWSCALEFACTOR | SET.ACT_POW_SCALE_FACTOR | ns=4;s=SET.ACT_POW_SCALE_FACTOR | FLOAT |  |  | 0.01 | NA | NA |  |  |  | Volt | MAINTENANCE | [6 empty] | ENG | This variable sets the scale factor for the active power 3 phase monitoring (W)
SET_THCU_APPARENTPOWSCALEFACTOR | THCU | APPARENTPOWSCALEFACTOR | SET.APPARENT_POW_SCALE_FACTOR | ns=4;s=SET.APPARENT_POW_SCALE_FACTOR | FLOAT |  |  | 0.01 | NA | NA |  |  |  | Volt Ampere | MAINTENANCE | [6 empty] | ENG | This variable sets the scale factor for the apparent power 3 phase monitoring (VA)
SET_THCU_REACTPOWSCALEFACTOR | THCU | REACTPOWSCALEFACTOR | SET.REACT_POW_SCALE_FACTOR | ns=4;s=SET.REACT_POW_SCALE_FACTOR | FLOAT |  |  | 0.01 | NA | NA |  |  |  | VAR | MAINTENANCE | [6 empty] | ENG | This variable sets the scale factor for the reactive power 3 phase monitoring (VAr)
SET_THCU_ENERGYSCALEFACTOR | THCU | ENERGYSCALEFACTOR | SET.ENERGY_SCALE_FACTOR | ns=4;s=SET.ENERGY_SCALE_FACTOR | FLOAT |  |  | 0.001 | NA | NA |  |  |  | Wh | MAINTENANCE | [6 empty] | ENG | This variable sets the scale factor for the energy 3 phase monitoring (Wh)
SET_THCU_COSPHISCALEFACTOR | THCU | COSPHISCALEFACTOR | SET.COSPHI_SCALE_FACTOR | ns=4;s=SET.COSPHI_SCALE_FACTOR | FLOAT |  |  | 0.001 | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the scale factor for the cosphi 3 phase monitoring
SET_THCU_FREQSCALEFACTOR | THCU | FREQSCALEFACTOR | SET.FREQ_SCALE_FACTOR | ns=4;s=SET.FREQ_SCALE_FACTOR | FLOAT |  |  | 0.1 | NA | NA |  |  |  | Hz | MAINTENANCE | [6 empty] | ENG | This variable sets the scale factor for the frequency 3 phase monitoring (Hz)
SET_THCU_ETHCATMASTERNETID | THCU | ETHCATMASTERNETID | SET.ETHCAT_MASTER_NETID | ns=4;s=SET.ETHCAT_MASTER_NETID | STRING |  |  | 5.24.54.134.2.1 | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the Net ID of the Master EtherCAT device of the THCU hardware configuration.
SET_THCU_TARGETNETID | THCU | TARGETNETID | SET.TARGET_NETID | ns=4;s=SET.TARGET_NETID | STRING |  |  | 192.168.4.111.1.1 | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the Net ID of the target device (THCU).
SET_THCU_SLAVEDEVICESNUMBER | THCU | SLAVEDEVICESNUMBER | SET.SLAVE_DEVICES_NUMBER | ns=4;s=SET.SLAVE_DEVICES_NUMBER | INT16 |  |  | 23 | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the number of slave devices connected to the EtherCAT master of the THCU hardware configuration
SET_THCU_SLAVEDEVICESBASEADDR | THCU | SLAVEDEVICESNUMBERBASEADDR | SET.SLAVE_DEVICES_BASEADDR | ns=4;s=SET.SLAVE_DEVICES_BASEADDR | INT16 |  |  | 1000 | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the root address of the slave devices connected to the EtherCAT master of the THCU hardware configuration
SET_THCU_MAXERRBUFFSIZE | THCU | MAXERRBUFFSIZE | SET.MAX_ERR_BUFF_SIZE | ns=4;s=SET.MAX_ERR_BUFF_SIZE | INT16 |  |  | 20 | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the maximum size of the error buffer.
SET_THCU_ERROR_INFO | THCU | ERROR_INFO | COMMAND.ERROR_INFO | ns=4;s=COMMAND.ERROR_INFO | INT16 |  |  | 0 | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ALL | This command enables access to the information about the required error (1 to n)
SET_THCU_AZPINTIMEOUT | THCU | AZPINTIMEOUT | SET.AZ_PIN_TIMEOUT | ns=4;s=SET.AZ_PIN_TIMEOUT | INT32 |  |  | 60 | NA | NA |  |  |  | NA | MAINTENANCE | [6 empty] | ENG | This variable sets the Timeout Duration for the AZ Stow Pin insertion/Extraction
SET_THCU_ELPINTIMEOUT | THCU | ELPINTIMEOUT | SET.EL_PIN_TIMEOUT | ns=4;s=SET.EL_PIN_TIMEOUT | INT32 |  |  | 60 | NA | NA |  |  |  | Sec | MAINTENANCE | [6 empty] | ENG | This variable sets the Timeout Duration for the EL Stow Pin insertion/Extraction

## CMD
Name of command | Actionee | Short name | ADS variable | OPC_UA node | OPC UA Data type | CMD/MODE value | Sampling Interval (s) | Default value | Alarm low | Alarm high | Withdraw alarm low | Withdraw alarm high | Unit | Operation modes | Expected execution time (s) | Maximum execution time (s) | IsMonitored | IsArchived | EngGUI | opGUI | Actor | Description
CMD_THCU_MOTORS400ON | THCU | MOTORS400VON | COMMAND.MOTORS_400V_ONOFF | ns=4;s=COMMAND.MOTORS_400V_ONOFF | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command activates the high voltage power supply to the AZ and EL drivers.
CMD_THCU_MOTORS400VOFF | THCU | MOTORS400VOFF | COMMAND.MOTORS_400V_ONOFF | ns=4;s=COMMAND.MOTORS_400V_ONOFF | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command deactivates the high voltage power supply to the AZ and EL drivers.
CMD_THCU_CAMERAON | THCU | CAMERAON | COMMAND.CAMERA_ONOFF | ns=4;s=COMMAND.CAMERA_ONOFF | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command powers on the camera cherenkov.
CMD_THCU_CAMERAOFF | THCU | CAMERAOFF | COMMAND.CAMERA_ONOFF | ns=4;s=COMMAND.CAMERA_ONOFF | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | The command powers off the camera cherenkov
CMD_THCU_DATALOGON | THCU | DATALOGON | COMMAND.DATA_LOGGER_ONOFF | ns=4;s=COMMAND.DATA_LOGGER_ONOFF | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | The command powers on the data logger
CMD_THCU_DATALOGOFF | THCU | DATALOGOFF | COMMAND.DATA_LOGGER_ONOFF | ns=4;s=COMMAND.DATA_LOGGER_ONOFF | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | The command powers off the data logger
CMD_THCU_M1BOXON | THCU | M1BOXON | COMMAND.M1_ONOFF | ns=4;s=COMMAND.M1_ONOFF | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command powers on the M1 boxes. All the boxes are powered on.
CMD_THCU_M1BOXOFF | THCU | M1BOXOFF | COMMAND.M1_ONOFF | ns=4;s=COMMAND.M1_ONOFF | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command powers off the M1 boxes
CMD_THCU_M2BOXON | THCU | M2BOXON | COMMAND.M2_ONOFF | ns=4;s=COMMAND.M2_ONOFF | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command powers on the M2 box. Actuators encoders and switches are powered on with this command.
CMD_THCU_M2BOXOFF | THCU | M2BOXOFF | COMMAND.M2_ONOFF | ns=4;s=COMMAND.M2_ONOFF | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command powers of the M2 box
CMD_THCU_PMCON | THCU | PMCON | COMMAND.PMC_ONOFF | ns=4;s=COMMAND.PMC_ONOFF | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command powers on the Pointing Monitor Camera (PMC)
CMD_THCU_PMCOFF | THCU | PMCOFF | COMMAND.PMC_ONOFF | ns=4;s=COMMAND.PMC_ONOFF | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command powers off the PMC
CMD_THCU_CAMERACONTROLON | THCU | CAMERACONTROLON | COMMAND.CAMERA_TH_CONTROL_ONOFF | ns=4;s=COMMAND.CAMERA_TH_CONTROL_ONOFF | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command powers on the Camera Thermal Control device
CMD_THCU_CAMERACONTROLOFF | THCU | CAMERACONTROLOFF | COMMAND.CAMERA_TH_CONTROL_ONOFF | ns=4;s=COMMAND.CAMERA_TH_CONTROL_ONOFF | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command powers off the Camera Thermal Control device
CMD_THCU_SQMON | THCU | SQMON | COMMAND.SQM_ONOFF | ns=4;s=COMMAND.SQM_ONOFF | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command powers on the Sky Quality Meter (SQM)
CMD_THCU_SQMOFF | THCU | SQMOFF | COMMAND.SQM_ONOFF | ns=4;s=COMMAND.SQM_ONOFF | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command powers off the SQM
CMD_THCU_UVSIPMON | THCU | UVSIPMON | COMMAND.UVSIPM_ONOFF | ns=4;s=COMMAND.UVSIPM_ONOFF | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command switches the UVSIPM assembly on
CMD_THCU_UVSIPMOFF | THCU | UVSIPMOFF | COMMAND.UVSIPM_ONOFF | ns=4;s=COMMAND.UVSIPM_ONOFF | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command switches the UVSIPM assembly off
CMD_THCU_UVSCOPEON | THCU | UVSCOPEON | COMMAND.UVSCOPE_ONOFF | ns=4;s=COMMAND.UVSCOPE_ONOFF | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command switches the UVSCOPE assembly on
CMD_THCU_UVSCOPEOFF | THCU | UVSCOPEOFF | COMMAND.UVSCOPE_ONOFF | ns=4;s=COMMAND.UVSCOPE_ONOFF | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command switches the UVSCOPE assembly off
CMD_THCU_AZSTOWPININ | THCU | AZSTOWPININ | COMMAND.AZSTOW_IN | ns=4;s=COMMAND.AZSTOW_IN | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | The command the isertion of the stow pin to block the AZ axis
CMD_THCU_AZSTOWPINOUT | THCU | AZSTOWPINOUT | COMMAND.AZSTOW_OUT | ns=4;s=COMMAND.AZSTOW_OUT | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | The command the extraction of the stow pin to free the AZ axis to move.
CMD_THCU_ELSTOWPININ | THCU | ELSTOWPININ | COMMAND.ELSTOW_IN | ns=4;s=COMMAND.ELSTOW_IN | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | The command the isertion of the stow pin to block the EL axis
CMD_THCU_ELSTOWPINOUT | THCU | ELSTOWPINOUT | COMMAND.ELSTOW_OUT | ns=4;s=COMMAND.ELSTOW_OUT | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | The command the extraction of the stow pin to free the EL axis to move.
CMD_THCU_AMCUON | THCU | AMCUON | COMMAND.AMCU_ONOFF | ns=4;s=COMMAND.AMCU_ONOFF | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | The command powers on the ACMU.
CMD_THCU_AMCUOFF | THCU | AMCUOFF | COMMAND.AMCU_ONOFF | ns=4;s=COMMAND.AMCU_ONOFF | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command powers off the ACMU.
CMD_THCU_TCUON | THCU | TCUON | COMMAND.TCU_ONOFF | ns=4;s=COMMAND.TCU_ONOFF | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | The command powers on the Telescope Control Unit (TCU)
CMD_THCU_TCUOFF | THCU | TCUOFF | COMMAND.TCU_ONOFF | ns=4;s=COMMAND.TCU_ONOFF | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | The command powers off the TCU
CMD_THCU_SQMPMCHEATEON | THCU | SQMPMCHEATEON | COMMAND.SQM_PMC_HEATER_ONOFF | ns=4;s=COMMAND.SQM_PMC_HEATER_ONOFF | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command gives power to the heater installed in the SQM/PMC assembly.
CMD_THCU_SQMPMCHEATEOFF | THCU | SQMPMCHEATEOFF | COMMAND.SQM_PMC_HEATER_ONOFF | ns=4;s=COMMAND.SQM_PMC_HEATER_ONOFF | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command switches off the heater.
CMD_THCU_SIRENALARMON | THCU | SIRENALARMON | COMMAND.SIREN_ALARM_ONOFF | ns=4;s=COMMAND.SIREN_ALARM_ONOFF | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command switches on the Siren Alarm when the TCU is in ONLINE (IDLE) for 5 seconds
CMD_THCU_SIRENALARMOFF | THCU | SIRENALARMOFF | COMMAND.SIREN_ALARM_ONOFF | ns=4;s=COMMAND.SIREN_ALARM_ONOFF | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command switches off the Siren Alarm.
CMD_THCU_AZ_ENABLE | THCU | AZ_ENABLE | COMMAND.AZ_ENABLE | ns=4;s=COMMAND.AZ_ENABLE | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command enables the AZ drives giving 24V to the X10:1 and X10:6 clamps
CMD_THCU_AZ_DISABLE | THCU | AZ_DISABLE | COMMAND.AZ_ENABLE | ns=4;s=COMMAND.AZ_ENABLE | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command disables the AZ drives taking out 24V to the X10:1 and X10:6 clamps
CMD_THCU_EL_ENABLE | THCU | EL_ENABLE | COMMAND.EL_ENABLE | ns=4;s=COMMAND.EL_ENABLE | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command enables the EL drives giving 24V to the X10:1 and X10:6 clamps
CMD_THCU_EL_DISABLE | THCU | EL_DISABLE | COMMAND.EL_ENABLE | ns=4;s=COMMAND.EL_ENABLE | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command disables the EL drives taking out 24V to the X10:1 and X10:6 clamps
CMD_THCU_OVERRIDESAFETYON | THCU | OVERRIDESAFETYON | COMMAND.FORCE_OVERRIDE_SAFETY | ns=4;s=COMMAND.FORCE_OVERRIDE_SAFETY | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command enables the Override Function
CMD_THCU_OVERRIDESAFETYOFF | THCU | OVERRIDESAFETYOFF | COMMAND.FORCE_OVERRIDE_SAFETY | ns=4;s=COMMAND.FORCE_OVERRIDE_SAFETY | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ALL | This command disables the Override Function
CMD_THCU_ERROR_RESET | THCU | ERROR_RESET | COMMAND.ERROR_RESET | ns=4;s=COMMAND.ERROR_RESET | BOOLEAN | TRUE |  | FALSE | [5 empty] | MAINTENANCE | [6 empty] | ALL | This command empties the error buffer and reset all the error informations recorded.
CMD_THCU_INHIBITFAULT | THCU | INHIBITFAULT | COMMAND.INHIBIT_FAULT | ns=4;s=COMMAND.INHIBIT_FAULT | BOOLEAN | TRUE |  | FALSE | [5 empty] | FAULT/MAINTENANCE | [6 empty] | ALL | This command inhibits the Fault status in order to perform the transition into Maintenance.
CMD_THCU_INHIBITFAULTRESET | THCU | INHIBITFAULTRESET | COMMAND.INHIBIT_FAULT | ns=4;s=COMMAND.INHIBIT_FAULT | BOOLEAN | FALSE |  | FALSE | [5 empty] | FAULT/MAINTENANCE | [6 empty] | ENG | This command reset the Fault status
CMD_THCU_OVERTEMPAVOIDANCE | THCU | OVERTEMPAVOIDANCE | COMMAND.OVERRIDE_TEMP_AVOIDANCE | ns=4;s=COMMAND.OVERRIDE_TEMP_AVOIDANCE | BOOLEAN | TRUE |  | FALSE | [5 empty] | MAINTENANCE | [6 empty] | ENG | This command provides to switch-on the AMCU and TCU devices even if the Temperature in the LPC is outside the operational range
CMD_THCU_MANCONFIGPAR | THCU | MANCONFIGPAR | COMMAND.MAN_CONFIG_PAR | ns=4;s=COMMAND.MAN_CONFIG_PAR | BOOLEAN | TRUE |  | FALSE | [5 empty] | MAINTENANCE | [6 empty] | ENG | This command enables the manual set up of the THCU configuration parameters (from GUI or TCS)
CMD_THCU_SAVECONFIGPAR | THCU | SAVECONFIGPAR | COMMAND.SAVE_CONFIG_PAR | ns=4;s=COMMAND.SAVE_CONFIG_PAR | BOOLEAN | TRUE |  | FALSE | [5 empty] | MAINTENANCE | [6 empty] | ENG | This command modifies the file of the THCU configuration parameters (from GUI or TCS)
CMD_THCU_LOADCONFIGPAR | THCU | LOADCONFIGPAR | COMMAND.LOAD_CONFIG_PAR | ns=4;s=COMMAND.LOAD_CONFIG_PAR | BOOLEAN | TRUE |  | FALSE | [5 empty] | MAINTENANCE | [6 empty] | ENG | This command loads the new file of the THCU configuration parameters (from GUI or TCS)
CMD_THCU_RESETSYSTEM | THCU | RESETSYSTEM | COMMAND.RESET_SYSTEM | ns=4;s=COMMAND.RESET_SYSTEM | BOOLEAN | TRUE |  | FALSE | [5 empty] | MAINTENANCE | [6 empty] | ENG | This command performs the reset of the system
CMD_THCU_STOWEMERGSTOP | THCU | STOWEMERGSTOP | COMMAND.STOW_EMERGENCY_STOP | ns=4;s=COMMAND.STOW_EMERGENCY_STOP | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE | [6 empty] | ENG | This commands stops the insertion or the extraction of the stow pins
CMD_THCU_OVERRIDE_PIN_ALARM_ON | THCU | OVERRIDE_PIN_ALARM_ON | COMMAND.OVERRIDE_PIN_ALARM | ns=4;s=COMMAND.OVERRIDE_PIN_ALARM | BOOLEAN | TRUE |  | FALSE | [5 empty] | ONLINE/MAINTENANCE | [6 empty] | ENG | This command enable the AZ/EL Stow pin insertion/extraction when an Alarm is present
CMD_THCU_OVERRIDE_PIN_ALARM_OFF | THCU | OVERRIDE_PIN_ALARM_OFF | COMMAND.OVERRIDE_PIN_ALARM | ns=4;s=COMMAND.OVERRIDE_PIN_ALARM | BOOLEAN | FALSE |  | FALSE | [5 empty] | ONLINE/MAINTENANCE | [6 empty] | ENG | This command disable the AZ/EL Stow pin insertion/extraction when an Alarm is present

## MODE
Name of command | Actionee | Short name | ADS variable | OPC_UA node | OPC UA Data type | CMD/MODE value | Sampling Interval (s) | Default value | Alarm low | Alarm high | Withdraw alarm low | Withdraw alarm high | Unit | Operation modes | Expected execution time (s) | Maximum execution time (s) | IsMonitored | IsArchived | EngGUI | opGUI | Actor | Description
MODE_THCU_GO_STANDBY | THCU | GO_STANDBY | COMMAND.COMMAND_THCU | ns=4;s=COMMAND.COMMAND_THCU | INT16 | 101 |  | 0 | [5 empty] | LOADED/ONLINE/MAINTENANCE | [6 empty] | ALL | This mode activates all the procedures to bring the THCU in the STANBY status.
MODE_THCU_GO_ONLINE | THCU | GO_ONLINE | COMMAND.COMMAND_THCU | ns=4;s=COMMAND.COMMAND_THCU | INT16 | 102 |  | 0 | [5 empty] | STANDBY | [6 empty] | ALL | This mode activates all the procedures to bring the THCU in the ONLINE status.
MODE_THCU_GO_LOADED | THCU | GO_LOADED | COMMAND.COMMAND_THCU | ns=4;s=COMMAND.COMMAND_THCU | INT16 | 100 |  | 0 | [5 empty] | STANDBY | [6 empty] | ALL | This mode activates all the procedures to bring the THCU in the LOADED status.
MODE_THCU_GO_MAINTENANCE | THCU | GO_MAINTENANCE | COMMAND.COMMAND_THCU | ns=4;s=COMMAND.COMMAND_THCU | INT16 | 105 |  | 0 | [5 empty] | STANDBY/ONLINE/FAULT | [6 empty] | ALL | This mode activates all the procedures to bring the THCU in the MAINTENANCE status.