## Main
Assembly | Description | Device Name | OPC UA address | Beckhoff AMS Net Id | ICD | ICD Date | PMCDeviceConnector | discoveryServerUrl
WS | Weather Station (WS) opc-ua interface | WeatherStation | opc.tcp://10.10.1.19:62650/OPCUA/AMA_WS_Server |  | ASTRI_MINI_ARRAY | 2022-08-21 | WeatherStationConnector | opc.tcp://192.168.100.128:48400

## GET
Name of command | Device Name | Short name | ADS variable | OPC_UA node | OPC UA Data type | CMD/MODE value | Sampling Interval (s) | Default value | Alarm low | Alarm high | Withdraw alarm low | Withdraw alarm high | Unit | Operation modes | Expected execution time (s) | Maximum execution time (s) | IsMonitored | IsArchived | EngGUI | OpGUI | Description
GET_WS_EXTTMP | WS | EXTTMP |  | ns=2;s=ws_exttmp | Double |  | 5 |  | -15 | 60 |  |  | ^C |  | 1 | 2 | yes | yes | Y | Y | Value of external temperature, expressed in degrees Celsius.
GET_WS_DEWPOINT | WS | DEWPOINT |  | ns=2;s=ws_dewpoint | Double |  | 5 | [5 empty] | ^C |  | 1 | 2 | yes | yes | Y | Y | Value of the dewpoint, expressed in degrees Celsius
GET_WS_WINDDIR | WS | WINDDIR |  | ns=2;s=ws_winddir | Int32 |  | 5 |  | 0 | 360 |  |  | deg |  | 1 | 2 | yes | yes | Y | Y | wind direction value in deg (0 deg= in no wind data)
GET_WS_WINDIR10M | WS | WINDIR10M |  | ns=2;s=ws_windir10m | Int32 |  | 5 |  | 0 | 360 |  |  | deg |  | 1 | 2 | yes | yes | Y | Y | wind direction for the 10-min wind guest (0 deg = in no wind data)
GET_WS_WINDSPD | WS | WINDSPD |  | ns=2;s=ws_windspd | Double |  | 5 |  | 0 | 200 |  |  | Km/h |  | 1 | 2 | yes | yes | Y | Y | wind speed value
GET_WS_WINDGUST10M | WS | WINDGUST10M |  | ns=2;s=ws_windgust10m | Double |  | 5 |  | 0 | 200 |  |  | km/h |  | 1 | 2 | yes | yes | Y | Y | Max value of the wind gust in the last 10 minutes
GET_WS_WND10AVG | WS | WND10AVG |  | ns=2;s=ws_win10avg | Double |  | 5 |  | 0 | 120 |  |  | KM/h |  | 1 | 2 | yes | yes | Y | Y | mean wind speed in the last 10 minutes
GET_WS_SOLARRAD | WS | SOLARRAD |  | ns=2;s=ws_solarrad | Int32 |  | 5 |  | 0 | 1500 |  |  | W/m2 |  | 1 | 2 | yes | yes | Y | Y | value of the solar radiance
GET_WS_EXTUMDY | WS | EXTUMDY |  | ns=2;s=ws_extumdy | Int32 |  | 5 |  | 2 | 90 |  |  | % |  | 1 | 2 | yes | yes | Y | Y | external relative humidity
GET_WS_RAINRATE | WS | RAINRATE |  | ns=2;s=ws_rainrate | Double |  | 5 |  | 0 | 999 |  |  | mm/h |  | 1 | 2 | yes | yes | Y |  | rainfall rate
GET_WS_RAINDAILY | WS | RAINDAILY |  | ns=2;s=ws_dailyrain | Double |  | 5 |  | 0 | 999 |  |  | mm |  | 1 | 2 | yes | yes | Y |  | day rain
GET_WS_RAIN1H | WS | RAIN1H |  | ns=2;s=ws_rain1h | Double |  | 5 |  | 0 | 999 |  |  | mm |  | 1 | 2 | yes | yes | Y |  | last hour rain
GET_WS_RAIN15M | WS | RAIN15M |  | ns=2;s=ws_rain15m | Double |  | 5 |  | 0 | 999 |  |  | mm |  | 1 | 2 | yes | yes | Y |  | last 15-min rain
GET_WS_BAROMTR | WS | BAROMTR |  | ns=2;s=ws_baromtr | Double |  | 5 |  | 0 | 9999 |  |  | hPa |  | 1 | 2 | yes | yes | Y | Y | value of the atmospheric pressure
GET_WS_BARTREND | WS | BARTREND |  | ns=2;s=ws_bartrend | String |  | 5 | [7 empty] | 1 | 2 | yes | yes | Y |  | Current 3-hour barometer trend: 1 - Falling Rapidly 2 - Falling Slowly 3 - Steady 4 - Rising Slowly 5 - Rising Rapidly 6 - No trend info is available 7 - Insufficient data to determine Bar-Trend
GET_WS_TBATTSTS | WS | TBATTSTS |  | ns=2;s=ws_tbattsts | Int32 |  | 5 |  | 1 | 9999 |  |  |  |  | 1 | 2 | yes | yes | Y |  | battery status of the transmitter
GET_WS_CBATTVOLT | WS | CBATTVOLT |  | ns=2;s=ws_cbattvolt | Double |  | 5 |  | 0 | 5 |  |  | V |  | 1 | 2 | yes | yes | Y |  | voltage of the console battery
GET_WS_STORMRAIN | WS | STORMRAIN |  | ns=2;s=ws_stormrain | Double |  | 5 |  | 0 | 999 |  |  | mm |  | 1 | 2 | yes | yes | Y |  | Storm rain displays the rain total of the last rain event
GET_WS_STARTSTORM | WS | STARTSTORM |  | ns=2;s=ws_startstorm | String |  | 5 | [7 empty] | 1 | 2 | yes | yes | Y |  | date of the beginning of a rain fall
GET_WS_UPDATETIME | WS | UPDATETIME |  | ns=2;s=ws_updatetime | Int32 |  | 5 | 5 | 2 | 999 |  |  | sec |  | 1 | 2 | yes | no | Y |  | Update time
GET_WS_EXECRESULT | WS | EXECRESULT |  | ns=2;s=ws_execresult | Int32 |  |  | 0 | -999 | 999 |  |  |  |  | 1 | 2 | yes | no | Y |  | result of the exec command, a value different from zero means: command not executed
GET_WS_RS232CONFIG | WS | RS232CONFIG |  | ns=2;s=ws_rs232config | string | [9 empty] | 1 | 2 | yes | no | Y |  | return the com port configuration: COM4 BaudRate=19200 DataBits=8 StopBits=1 Parity=0 FlowControl=0
GET_WS_ISOTSTAMP | WS | ISOTSTAMP |  | ns=2;s=ws_isotstamp | string | [9 empty] | 1 | 2 | yes | yes | Y |  | return the time stamp in the ISO8601 format
GET_WS_STATUS | WS | STATUS |  | ns=2;s=ws_status | Int32 |  | 5 | [7 empty] | 1 | 2 | yes | yes | Y |  | Status of the WS: 0:loaded; 7:fault; 10:online-communication error 7 = FAULT 10 = COMMUNICATION_ERROR
GET_WS_ERROR_NUMBER | WS | ERROR_NUMBER |  | ns=2;s=ws_error_number | int32 |  | 5 | 0 | [6 empty] | 1 | 2 | yes | no | Y |  | The monitor reports the number of errors that has been occurred
GET_WS_ERROR_INFORMATION | WS | ERROR_INFORMATION |  | ns=2;s=ws_error_information | string |  | 5 | [7 empty] | 1 | 2 | yes | no | Y |  | The monitor reports the information about the required error. The format is (code,origin,class,timestamp) . Class filed 1: Alarm 2: Error 3:Warning . The timestamp is in UTC format. Origin and Code are available in a separate document.
GET_WS_ERROR_RECOVERING | WS | ERROR_RECOVERING |  | ns=2;s=ws_error_recovering | string |  | 5 | [7 empty] | 1 | 2 | yes | no | Y |  | The monitor shows the lists of error that has been occurred and recovered. (1:True,2:False,...). The False status means that the corresponding error has been recovered.
GET_WS_ERROR_NUMBER_RECOVERED | WS | ERROR_NUMBER_RECOVERED |  | ns=2;s=ws_error_number_recovered | int32 |  | 5 | 0 | [6 empty] | 1 | 2 | yes | no | Y |  | The monitor reports the number of errors that has been recovered
GET_WS_ERROR_NUMBER_OUTOFRANGE | WS | ERROR_NUMBER_OUTOFRANGE |  | ns=2;s=ws_error_number_outofrange | boolean |  | 5 | false | [6 empty] | 1 | 2 | yes | no | Y |  | The monitor reports the number of errors that has been recovered
GET_WS_HEARTBEAT | WS | HEARTBEAT |  | ns=2;s=ws_heartbeat | int32 |  | 1 | 0 | [6 empty] | 1 | 1 | yes | no | Y
GET_WS_UV | WS | UV |  | ns=2;s=ws_uv | Double |  | 5 | 0 |  |  |  |  | W/m2 |  | 1 | 2 | yes | yes | Y | Y | UV value Watt/m2
GET_WS_INSTMP | WS | INSTMP |  | ns=2;s=ws_instmp | Double |  | 5 |  | -15 | 60 |  |  | ^C |  | 1 | 2 | yes | yes | Y | Y | Value of inside temperature, expressed in degrees Celsius.
GET_WS_INSUMDY | WS | INSUMDY |  | ns=2;s=ws_insumdy | Double |  | 5 |  | 2 | 90 |  |  | % |  | 1 | 2 | yes | yes | Y | Y | inside relative humidity
GET_WS_APP_NAME | WS | APP_NAME |  | ns=2;s=serverApplicationName | String |  |  | AMA_WS_Server | [8 empty] | yes | no | Y |  | Server Application Name
GET_WS_OPCUA_PORT | WS | OPCUA_PORT |  | ns=2;s=opcuaPort | Int32 |  |  | 52620 | [8 empty] | yes | no | Y |  | Server Port no.
GET_WS_WEB_PORT | WS | WEB_PORT |  | ns=2;s=webPort | Int32 |  |  | 0 | [8 empty] | yes | no | Y |  | Web Server Port no. (not used)
GET_WS_APP_START_TIME | WS | APP_START_TIME |  | ns=2;s=startTime | String | [11 empty] | yes | no | Y |  | Server run start time
GET_WS_SERIAL_NUMBER | WS | SERIAL_NUMBER |  | ns=2;s=serialNumber | String |  |  | WS1 | [8 empty] | yes | no | Y |  | Serial Number
GET_WS_ICD_FILE_NAME | WS | ICD_FILE_NAME |  | ns=2;s=ICDName | String | [11 empty] | yes | no | Y |  | Table file name (not used)
GET_WS_PROSYS_SDK_VERSION | WS | PROSYS_SDK_VERSION |  | ns=2;s=prosysSdkVersion | String | [11 empty] | yes | no | Y |  | Prosys SDK version
GET_WS_CURRENT_SESSION_NUMBER | WS | CURRENT_SESSION_NUMBER |  | ns=2;s=currentSessionNumber | INT32 | [11 empty] | yes | no | Y |  | N0. of opcua clients connected
GET_WS_SESSIONS_NAME | WS | SESSIONS_NAME |  | ns=2;s=sessionsName | String[100] | [11 empty] | yes | no | Y |  | sessions (clients) name
GET_WS_RANDOM_GENERATOR_CODE | WS | RANDOM_GENERATOR_CODE |  | ns=2;s=randomGeneratorCode | INT32 |  |  | 0 | [8 empty] | yes | no | Y |  | not used
GET_WS_VERBOSE_STATUS | WS | VERBOSE_STATUS |  | ns=2;s=verboseStatus | boolean |  |  | true | [8 empty] | yes | no | Y |  | verbose status

## SET
Name of command | Device Name | Short name | ADS variable | OPC_UA node | OPC UA Data type | CMD/MODE value | Sampling Interval (s) | Default value | Alarm low | Alarm high | Withdraw alarm low | Withdraw alarm high | Unit | Operation modes | Expected execution time (s) | Maximum execution time (s) | IsMonitored | IsArchived | EngGUI | OpGUI | Actor | Description
SET_WS_SETUPDATETIME | WS | SETUPDATETIME |  | ns=2;s=ws_setupdatetime | double |  |  | 5 | 4 | 999 |  |  | sec |  | 1 | 1 |  |  | Y | N | ENG | Change the WS update time (value >= 4)
SET_WS_ERROR_INDEX | WS | ERROR_INDEX |  | ns=2;s=ws_error_index | int32 |  |  | 0 | 0 | 9999 |  |  |  |  | 1 | 2 | no | no | Y | N | ALL | index of the retrieve error

## CMD
Name of command | Device Name | Short name | ADS variable | OPC_UA node | OPC UA Data type | CMD/MODE value | Sampling Interval (s) | Default value | Alarm low | Alarm high | Withdraw alarm low | Withdraw alarm high | Unit | Operation modes | Expected execution time (s) | Maximum execution time (s) | IsMonitored | IsArchived | EngGUI | OpGUI | Actor | Description
CMD_WS_EXEC | WS | EXEC |  | ns=2;s=ws_exec | double | 1 |  | 0 |  |  |  |  | -- | ONLINE |  |  |  |  | Y |  | ALL | Command to read WS values on demand
CMD_WS_UPDATESTOP | WS | UPDATESTOP |  | ns=2;s=ws_updatestop | Int32 | 1 |  | -1 |  |  |  |  | -- | ONLINE | 1 | 1 |  |  | Y |  | ALL | to stop the WS data update
CMD_WS_UPDATERESUME | WS | UPDATERESUME |  | ns=2;s=ws_updateresume | Int32 | 1 |  | -1 |  |  |  |  | -- | ONLINE | 1 | 1 |  |  | Y |  | ALL | to resume the WS data update
CMD_WS_SIM | WS | SIM |  | ns=2;s=ws_sim | Int32 | 1 |  | -1 |  |  |  |  | -- | ONLINE | 1 | 1 |  |  | Y |  | ENG | to start the simulation mode
CMD_WS_SERVERSHUTDOWN | WS | SERVERSHUTDOWN |  | ns=2;s=ws_servershutdown | Int32 | 1 |  | 0 |  |  |  |  | -- | ONLINE | 5 | 10 |  |  | Y |  | ENG | Execute the WS server shutdown if the value is set to 1
CMD_WS_ERROR_INFO | WS | ERROR_INFO |  | ns=2;s=ws_error_info | Int32 | 1 |  | 0 |  |  |  |  | -- | ONLINE | 1 | 1 |  |  | Y |  | ALL | This command enables access to the information about the required error.
CMD_WS_ERROR_RESET | WS | ERROR_RESET |  | ns=2;s=ws_error_reset | boolean | TRUE |  | FALSE |  |  |  |  | -- | ONLINE | 1 | 1 |  |  | Y |  | ALL | This command empties the error buffer and reset all the error informations recorded.

## MODE
Name of command | Device Name | Short name | ADS variable | OPC_UA node | OPC UA Data type | CMD/MODE value | Sampling Interval (s) | Default value | Alarm low | Alarm high | Withdraw alarm low | Withdraw alarm high | Unit | Operation modes | Expected execution time (s) | Maximum execution time (s) | IsMonitored | IsArchived | EngGUI | OpGUI | Actor | Description
MODE_WS_GO_LOADED | WS | GO_LOADED |  | ns=2;s=ws_state_transition | INT32 | 100 |  | 0 | [5 empty] | STANDBY |  |  |  |  | Y |  | ALL | This mode activates all the procedures to bring to LOADED status.
MODE_WS_GO_STANDBY | WS | GO_STANDBY |  | ns=2;s=ws_state_transition | INT32 | 101 |  | 0 | [5 empty] | ONLINE IDLE/LOADED |  |  |  |  | Y |  | ALL | This mode activates all the procedures to bring to STANDBY status.
MODE_WS_GO_ONLINE | WS | GO_ONLINE |  | ns=2;s=ws_state_transition | INT32 | 102 |  | 0 | [5 empty] | STANDBY |  |  |  |  | Y |  | ALL | This mode activates all the procedures to bring to ONLINE status.

## notes
Date | Version | Actionee
09 dec 2020 V1.6 | V16 (1.6) | add opcua node ws_heartbeat and ws_uv in the GET form - Add ns=2;s=ws_state_transition node for state_machine
2021-04-14 | V17 (1.7) | add folder serverInfo containing the node
ns=2;s=serverApplicationName
ns=2;s=opcuaPort
ns=2;s=webPort
ns=2;s=startTime
ns=2;s=serialNumber
ns=2;s=fileNameTable
ns=2;s=prosysSdkVersion
ns=2;s=currentSessionNumber
ns=2;s=sessionsName
ns=2;s=randomGeneratorCode
ns=2;s=verboseStatus
20May2021 | V171 (1.71) | changed fron tablefilename ti ICDName...
14Jun2021 |  | changed all int16 vars to int32
changed AssemblyName to WeatherStationSupervisor
15Dec2021 |  | changed MAIN form to the new ICD format
2022-02-17 | V172 (1.72) | Changed AUX to WS and eliminated WS_ from "Short name" columns
21-aug.22 | V200 (2.00) | new ICD format